## Slide 1: Solar Energy

## Slide 2: Application of solar energy that can be used
Solar technology was used to reduce the dependent on energy consumption from fuel in different sectors.
In this section we summarized some solar application that can be used.

## Slide 3: Application of solar energy that can be used
Solar Thermal Water heating systems
Households, public building (hotels, hospitals, universities, school), and factories are the main users of solar water heating systems.
Solar District Heating
District heating is one of heating systems that transfers & distributes heat that used in the residential industrial & commercial sectors for hot water heating, space heating, & industrial processes, it is very reliable, see figure.
The temperature of district heating supply water varies depending on the country weather, being for example 65-115° C.

## Slide 4: Solar District Heating
The temperature is at its lowest in summer and highest in winter, when heat is only needed for hot water.
It consists of heat production units, which could be a combination of heating-only plants, combined heat and power production plants, waste heat recovery plants, peaking and standby heat plants, primary heat distribution network, substations at the consumer connection points, end users secondary networks and installations for space heating and domestic hot water.

## Slide 5: Solar District Heating

## Slide 6: Integrated Collector Storage (ICS) System
ICS also called batch water heater, see figure the water is heated and stored inside the collector.
These systems are suitable only for warm climates where there is no risk of freezing.
ICS are made of one or more black tanks or tubes in an insulated glazed box.
Cold water first passes through the solar collector, which preheats the water, and then continues to the conventional backup water heater.
ICS systems are simple, reliable solar water heaters.

## Slide 7: Integrated Collector Storage (ICS) System
However, they should be installed only in climates with mild freezing because the collector itself or the outdoor pipes could freeze in severely cold weather.
Some recent work indicates that the problem with freezing pipes can be overcome in some cases by using freeze-tolerant piping in conjunction with a freeze-protection method.

## Slide 8: Integrated Collector Storage (ICS) System

## Slide 9: The Vacuum Tube Collector
A vacuum tube collector is composed of a series of evacuated glass tubes.
Inside the tube, an absorber plate, in contact with a pipe in which the heat transfer fluid flows, collects the solar energy.
Heat losses are low, owing to the insulating properties of the vacuum.
Therefore, the temperature can rise to over 100°C. This type of collector is particularly well adapted to applications that need high temperatures, see figure

## Slide 10: The Vacuum Tube Collector

## Slide 11: Concentrating Collectors
Concentrating collectors use mirrored surfaces to concentrate the sun's energy on an absorber called a receiver, see figure.
Concentrating collectors also achieve high temperatures, but unlike evacuated-tube collectors, they can do so only when direct sunlight is available.
The mirrored surface focuses sunlight collected over a large area onto a smaller absorber area to achieve high temperatures.

## Slide 12: Concentrating Collectors
Some designs concentrate solar energy into a focal point, while others concentrate the sun's rays along a thin line called the focal line.
The receiver is located at the focal point or along the focal line.
A heat-transfer fluid flows through the receiver and absorbs heat.

## Slide 13: Concentrating Collectors
These collectors reach much higher temperatures than flat-plate collectors.
However, concentrators can only focus direct solar radiation, with the result being that their performance is poor on hazy or cloudy days.
Concentrators perform best when pointed directly at the sun. To do this, these systems use tracking mechanisms to move the collectors during the day to keep them focused on the sun.

## Slide 14: Concentrating Collectors
Single-axis trackers move east to west; dual-axis trackers move east and west & north and south (to follow the sun throughout the year).
Concentrators are used mostly in commercial & industrial applications because they are expensive & because the trackers need frequent maintenance.

## Slide 15: Concentrating Collectors
Some residential solar energy systems use parabolic trough concentrating systems. These installations can provide hot water, space heating, & water purification.
Most residential systems use single axis trackers, which are less expensive & simpler than dual-axis trackers.
There are four basic types of concentrating collectors: Parabolic trough, parabolic dish, Power tower, Stationary concentrating collectors.

## Slide 16: Concentrating Collectors

## Slide 17: Concentrating Collectors (Almeria –Spain)

## Slide 18: Concentrating Collectors

## Slide 19: Space Heating and Cooling Systems
Heating a home with solar energy is not difficult in Palestine.
If done correctly the building will use 50 to 70 percent less energy during the heating season, have good day lighting & remain cool during the hottest summer months.
2 approaches can be used to heat a home with solar energy: An Active System or a Passive System.

## Slide 20: Space Heating and Cooling Systems
Active systems use mechanical equipment such as a pump or fan to move energy from collectors into the house.
Passive systems are much more common, simply relying on south facing windows to allow solar heat & light into the building, The figure shows the sun chart for space heating using passive solar systems

## Slide 21: Sun chart for space heating using passive solar systems

## Slide 22: Sun chart for space heating using passive solar systems
Space heating & cooling consume a huge amount of energy in all sectors in Palestine.
In order to reduce these quantities we can design our new building to include one of the following systems:

## Slide 23: Solar Window
Windows are one of the important elements in designing buildings because of their role in reducing the energy consumed in heating, cooling & lighting, also they are considered as a good & inexpensive solar collector.
The size of the windows, the types of glass used & the orientation are the basic techniques to derive the maximum benefit from solar windows.

## Slide 24: Solar Window
The best design is to make the windows facing the south to obtain the largest amount of solar energy especially in the winter when the sun is low in the sky while in the summer when the sun is high and its temperature is high.
Also, a several techniques can be used to reduce the excessive heat from entering through these windows, such as shading or the use of umbrellas.

## Slide 25: Solar Window
The shading helps to reduce heat gain in summer and heat loss at night, see figure

## Slide 26: Solar Window
New technologies are used in designing the windows that include selective coatings, & increasing window insulation properties lessened such concerns to help keep heat where it is needed.

## Slide 27: Solar Window
A high Solar Heat Gain Coefficient (SHGC) usually 0.60 or higher,to maximize heat gain is required in south-facing windows to be effective, to reduce conductive heat transfer the U-factor must be low (0.35 or less), & for good visible light transfer it is used a high visible transmittance (VT).

## Slide 28: Solar Window
SHGC refers to the portion of incident sunlight admitted through a window, & U-factor indicates the heat loss rate for the window assembly.
Shading from landscaping, overhangs, shutters, and solar window screens helps lower heat gain on windows that receive full sun.

## Slide 29: Solar Wall (or Trombe Wall)
Solar walls are simple systems used for space heating. These walls are also known as Trombe walls.
The diagram in figure shows how the collector operates. The solar radiation heats the outside of the solar wall. The heat slowly passes through the massive wall, & arrives at the inside surface of the wall several hours later to provide heat in the evening.

## Slide 30: Solar Wall (or Trombe Wall)
The glazed covering on the outside of the wall reduces heat loss, & allows more heat transfer to the inside space.
The vents shown at the top and bottom of the wall in this diagram are optional they allow heat to be transferred to the living space earlier in the day than occurs with an unvented solar wall.

## Slide 31: Solar Wall

## Slide 32: The characteristics of a solar wall as compared to a solar window
1- Its efficiency in collecting solar heat is not as high as a direct gain window of the same size.
2- Night heat losses are less than for direct gain windows.
3- Very simple : no fans, no ducts, no controllers.
4- Does not provide day lighting or views as a direct gain window would :this can be an advantage or disadvantage.
5- The inside surface of the wall can be used to some extent, but should not be covered with anything that reduces heat transfer from the wall to the living space.
6- Depending on the current wall construction, it may be easier to retrofit a solar wall than to retrofit a direct gain window, since no wall structural members are cut. The collectors can be used in new construction, or as a retrofit.

## Slide 33: SolarChimneys
This retrofit passive space heating device, called a Thermosiphoning Air Panel (TAP), uses the existing house wall as the major structural element.
The exterior finish is removed, new glass box structural sheathing added over the existing wall, and wood framing added to support the ribbed aluminum absorber plate (industrial siding material) & to support the field-installed insulated glass units.
The system shown uses 3 patio door replacement units as the aperture, creating 3 areas of absorber plate, each of which requires a high & a low vent through the house wall to allow the thermosiphoning action to occur.

## Slide 34: Solar Chimneys
The characteristics of the Solar Chimney see figure as compared to a solar window:
• It has roughly the same collection efficiency as a direct gain window.
• Night heat losses are less than for direct gain windows.
• Very simple no fans, no ducts, no controllers :uses natural convection.
• Does not provide day lighting or views as a direct gain window would this can be an advantage or disadvantage.
• The inside surface of the wall can be used for shelves etc. unlike a direct gain window.
• No structural changes to the wall framing are required, since no structural members are cut this can make it an easier retrofit than a direct gain window.

## Slide 35: Solar Chimneys

## Slide 36: Solar Chimneys
These are very cost effective energy collectors.
For example, a PV panel of the same size would cost 5 to 10 times more, and produce about one fifth as much energy! Depending on the materials used, & how good a scrounger you are, the payback period will usually be a year or two.

## Slide 37: Solar Roofs
Solar roofs, often called thermal storage roofs, see figure is similar to storage walls.
Waterbed-like bags of water, exposed to sunlight, collect, store and distribute heat. This heat passes freely down through the supporting ceiling to the house, gently warming it.
In summer, heat rises through the ceiling into the water, cooling the house. Then at night, the water is cooled by the radiation of its heat to the sky.

## Slide 38: Solar Roofs

## Slide 39: Solar Roofs
Movable insulation covers the ponds at night in winter, to trap heat inside, and during the day in summer, to shade the ponds while the sun is shining.
Generally, solar roof ponds are 8 to 12 inches deep. Roof ponds are always flat, but in northern buildings the glazing is often sloped to the south to capture the sun's low rays as well as to shed snow.
Under the sloped glass, the walls are well insulated and faced with materials that reflect the sunlight into the ponds.

## Slide 40: Greenhouse (Solarium)
Greenhouses are the most common solar rooms, see figure Conventional greenhouses, however, are not designed to take maximum advantage of the sun's energy.
Solar Room

## Slide 41: Greenhouse (Solarium)
The problem is that most are built with a single layer of glass, and so they lose more heat at night than they gain from the sun during the day.
Consequently, they need expensive auxiliary heat to keep the plants warm.
A solar greenhouse is designed both to maximize solar gain & to minimize heat loss.

## Slide 42: Under floor heating using solar water heating
Under floor heating & cooling is a form of central heating & cooling which uses heat conduction & radiant heat or cold for indoor climate control, rather than forced air heating which relies on convection, see figure.
Under Floor Hot Water System

## Slide 43: Under floor heating using solar water heating
Heat can be provided by circulating heated water or by electric cable, mesh, or film heaters.
This technique does not require hot water at high temperatures as the case for central heaters with radiators. Warm water at temperature around 30°C is good enough to make the room warm enough for residents.
This fact makes solar water heaters a good source of energy for this system as it is difficult to get higher temperatures in winter.

## Slide 44: * Solar Energy availability
Detailed information about solar radiation availability at any location is essential for the design & economic evaluation of solar energy system.
Various models based on available climatic data can be used to estimate the solar energy availability.

## Slide 45: Solar Energy Availability
The solar energy is in the form of electromagnetic radiation with the wavelengths ranging from about 0.3 μm to over 3 μm,
which correspond to Ultraviolet (less than 0.4 μm), Visible (0.4 and 0.7 μm), & Infrared (over 0.7 μm).
Most of this energy is concentrated in the visible & the near-infrared wavelength range 0.7

## Slide 46: Solar Energy Availability
Sun light passing through the atmosphere:
The total irradiance on a horizontal surface on Earth is also called Global Irradiance EG,hor.
It is the sum of the Direct Irradiance Edir,hor & the diffuse irradiance Ediff,hor on the horizontal surface:
EG,hor = Edir,hor + Ediff,hor

## Slide 47: Solar Energy Availability

## Slide 48: The air Mass ratio (AM)
Air Mass is the ratio of the path length of the sun's rays through the atmosphere when the sun is at a given angle (θ) to the zenith, to the path length when the sun is at its zenith. this leads to the definition:
AM =(L/d) = 1/sinαs = 1/cos θ,
αs: Sun Height (solar altitude or elevation)
AM is equal to 1, if the light is passing vertically through the atmosphere.
The AM value outside the atmosphere is zero.

## Slide 49: The air Mass ratio (AM)

## Slide 50: Earth Sun Relationships
The extraterrestrial solar radiation varies throughout the year because of the variation in the Earth–sun distance (D) as:
N=Day number (starting from January 1 as 1)

## Slide 51: Sun - Earth Relationships

## Slide 52: Solar Radiation on A surface
As solar radiation passes through the atmosphere, some of it is absorbed by air & water vapor, while some gets scattered by molecules of air, water vapor, & dust particles.
The part of solar radiation that reaches the surface of the Earth with essentially no change in direction is called direct or beam normal radiation, IbN. The scattered radiation reaching the surface from the atmosphere is called diffuse radiation, Id. IbN can be calculated from the extraterrestrial solar irradiance, I, & the atmospheric optical depth d as:

## Slide 53: Solar Radiation on A surface
where θ (z) is the solar zenith angle (angle between the sun rays and the vertical).

## Slide 54: Solar Radiation on A surface
To account for the differences in local conditions from the average sea level conditions IbN Equation is modified by a parameter called Clearness Number, Cn, as:
values of Cn vary between 0.85 and 1.15. Total incident solar radiation on a horizontal surface is given by:

## Slide 55: Solar Radiation on A surface
where θ (z) is the solar zenith angle and C is called the sky diffuse factor
Solar Radiation on tilted angle:
For a tilted surface with angle of incidence θ, the total incident solar radiation is given by:

## Slide 56: Solar Radiation on A surface
α : Solar altitude angle
β: Panel tilt angle (S)
θ: Incident angle (i)
where ρ is the reflectivity of the surroundings.
For ordinary ground or grass, ρ is approximately 0.2 while for ground covered with snow it is approximately 0.8.

## Slide 57: Direct Irradiation on tilted surfaces
The horizontal surface in Figure below with the area Ahor receives the same radiant power Φ as a smaller area As which is normal to the incoming sunlight.

## Slide 58: Direct Irradiation on tilted surfaces
It becomes apparent that the direct normal or beam irradiance Idir,s on a surface perpendicular to the path of the light is higher than the direct irradiance Idir,hor on a horizontal surface; this fact is taken into account when planning solar energy systems. Inclining the surface of the system increases the energy yield, especially at high latitudes with low solar height angles.

## Slide 59: Solar Radiation Measurements
2 basic types of instruments are used in measurements of solar radiation:
Pyranometer: An instrument used to measure global (direct and diffuse) solar radiation on a surface. This instrument can also be used to measure the diffuse radiation by blocking out the direct radiation with a shadow band.
Pyrheliometer: This instrument is used to measure only the direct solar radiation on a surface normal to the incident beam. It is generally used with a tracking mount to keep it aligned with the sun.

## Slide 60: Defining terms
Diffuse radiation: Scattered solar radiation coming from the sky.
Direct or beam normal radiation: Part of solar radiation coming from the direction of the sun on a surface normal to the sun’s rays.
Extraterrestrial solar radiation: Solar radiation outside Earth’s Atmosphere
Insolation: Incident solar radiation measured as W/m2
Solar constant: Extraterrestrial solar radiation at the mean Earth– sun distance.