## Slide 1: Solar Thermal Engines (Electricity Generation)
You need to concentrate the solar light

## Slide 2: Concentrating -Why?
To reflect and focus more direct solar radiation to a smaller area in order to….
Generate more heat (then generating electricity)
Generate more electricity
This is called
Concentrated Solar Power (CSP) Plants
This is called
Concentrated Photovoltaics (CPV)

## Slide 3: Concentrating -How?
Point focus
Line focus
Power tower
Dish
Parabolic
Fresnel

## Slide 4: Concentrating -How?
Overview
  http://www.youtube.com/watch?v=rO5rUqeCFY4
2GreenEnergy
  http://www.youtube.com/watch?v=8sLej0oD1Ak
Shams 1
  http://www.youtube.com/watch?v=HY3KoieEcs0
  https://www.youtube.com/watch?v=IzXZtQIBVbU
  https://www.youtube.com/watch?v=eWzQjZtE_XM
  https://www.youtube.com/watch?v=U3b9VZAjLt0
  https://www.youtube.com/watch?v=S_te2Yh5QAc

## Slide 5: Comparison
 | Dish | Power Tower | Line Focus
How | Parabolic 3D | Heliostat | Parabolic 2D or linear Fresnel
Tracking | 2 axis | 2 axis | 1 axis (east to west)
Focal Length | ~ 1-4 m | ~ Hundreds | ~ 3 m
Concentrating Ratio | ~ 3000 | ~ 800 | ~ 30-40
Notes: Heliostat: rotating mirror
Line focus can get to 150-200 c while the dish can reach 700-1000 c

## Slide 6: Parabola profiles for radiation concentration
Parabola profile with ray path
segmented parabola profile (Fresnel) with ray path
c) and d) profiles extruded from profiles a) and b)
e) and f) rotational solids of profiles a) and b)
The more flat the parabola, the more distant is the focal point (or the focal plane of the image of the sun) from the apex of the parabola.

## Slide 7: Dish - Concept
Uses a mirrored parabolic dish
Focus on a thermal receiver
Transfer heat to engine/generator
https://www.eeremultimedia.energy.gov/solar/sites/default/files/dish_receivers_598x300.JPG
Stirling engine – uses cyclic compression and expansion of air or other gas to move pistons and create mechanical power.

## Slide 8: Dish - Actual
http://www.volker-quaschning.de/fotos/psa/Dish1_1024x768.jpg

## Slide 9: The First Solar Engine
Built in 1870 by Augustin Mouchot, a mathematics professor, and his assistant Abel Pifre.
Steam boiler mounted at the focus and steam pipes ran down to reciprocating engine on the ground.

## Slide 10: Power Tower - Concept
Uses a large field of heliostats to focus and concentrate the sunlight onto the receiver on the top of a tower
The fluid can be water or molten salt
Figure 7-1

## Slide 11: Power Tower - Actual
http://www.inhabitat.com/wp-content/uploads/solarseville.jpg

## Slide 12: Line Focus – concept
Generally, the line focus system is oriented in the north-south direction, with one axis tracking in the east-west direction.
https://www.eeremultimedia.energy.gov/solar/sites/default/files/parabolic_troughs_600x281.JPG

## Slide 13
http://www.thenational.ae/
http://www.nrel.gov/csp/troughnet/images/illustration_trough_sunlight.gif

## Slide 14: Linear Fresnel
http://www.drive-and-control.com/dcen/wp-content/uploads/2012/10/32_KnowHow-3.jpg
http://solardawn.com.au/wp-content/gallery/sidebar/tech-web-7.jpg

## Slide 15: Linear Fresnel Power plant
Figure Linear Fresnel power plant

## Slide 16
Site requirments
  Solar radiation (Insolation)
  Persentage of area cover by solar collector
2. Collectores
  Model of array (Fixed or Track)
  Concentration ratio
  Average solar enrgy striking the collector per day
  15 % of insolation striking the collector convert to electricity
3. Output power depend on
  Time of the day
  Season
  Clouds cover
    10-15 % reduction from thin cirrus
    50-70 % reduction from dense cumulus
Figure Map of world solar energy by NASA
General topic for design

## Slide 17: Reflector materials
Material | Reflectivity ()
Copper | 0.75
Aluminized type-C Mylar (from Mylar side) | 0.76
Gold | 0.76±0.03
Various aluminum surfaces-range | 0.82-0.92
Anodized aluminum | 0.82±0.05
Aluminized acrylic, second surface | 0.86
Black-silvered water-white plate glass | 0.88
Silver (unstable as a front surface mirror) | 0.94±0.02

## Slide 18: Concentration ratio
Concentration ratio is a term used to describe how well the collector concentrates the light energy incident on it. Two common ratios are used; Optical and Geometric:
Parallel sun rays being concentrated
onto the focal line of the collector
Ir is solar flux on receiver
Ic is solar flux on collector
Ar is area of receiver
Aa is area of collector
Optical concentration ratio (CRO ) relates directly to lens or reflector quality
Collector
Receiver

## Slide 19: Energy Calculation
Energy balance
  Useful energy delivered to the receiver = Energy delivered from the collector – energy lost from the receiver
Where:
qc - useful energy delivered by the collector to the receiver
o - optical efficiency
UL - overall heat transfer coefficient
Tr - receiver temperature
Ta - ambient temperature
The optical efficiency is not the same as the optical Concentration Ratio. The optical efficiency takes into account factors like the absorbtance of the receiver, the reflectance of the concentrator, and the transmittance of the glass envelope over the receiver (if one is present).

## Slide 20: Efficiency Calculation
Approach 1: Energy delivered to the receiver Ratio of the energy at the received by the energy at the collector. | Approach 2: Energy generated in the receiver
Where:
is mass flow rate of fluid inside the receiver
is specific heat of the fluid
Tout is outlet temperature of the fluid
Tin is inlet temperature of the fluid

## Slide 21: Tracking mode
Figure Tracking of the sun by a parabolic trough collector with the collector axis oriented north-south

## Slide 22: Characteristics of solar thermal electric power systems
 | Parabolic Trough | Power Tower | Dish/Engine
Size | 30-320 MW* | 10-200 MW* | 5-25 kW*
Operating Temperature | 390 ºC | 565 ºC | 750 ºC
Annual Capacity Factor** | 23-50%* | 20-77%* | 25%
Peak Efficiency | 20%(d) | 23%(p) | 29.4%(d)
Net Annual Efficiency | 11(d’)-16%* | 7(d’)-20%* | 12-25%*(p)
Commercial Status Technology Development Risk Storage Available Hybrid Designs | Commercially Available Low Limited Yes | Scale-up Demonstration Medium Yes Yes | Prototype Demonstration High Battery Yes
Cost $/m2 $/W $/Wp† | 630-275* 4.0-2.7* 4.0-1.3* | 475-200* 4.4-2.5* 2.4-0.9* | 3,100-320* 12.6-1.3* 12.6-1.1*
* Values indicate changes over the 1997-2030 timeframe.
** Increases in capacity factor due to the use of thermal storage.
† $/Wp removes the effect of thermal storage (or hybridization for dish/engine).
(p) = predicted; (d) = demonstrated; (d’) = has been demonstrated, out years are predicted values

## Slide 23
NEVADA SOLAR ONE, Boulder City, Nevada, USA
Parabolic trough (Oil)
64 MW(e) nominal
ANDASOL 1 + 2, Granada, Spain
Parabolic trough (Oil)
50 MW(e) each