## Slide 1: Ch.5 Lighting
Dr. Mohammed Alsayed

## Slide 2: Introduction
In many cases, lighting can be improved and operation costs can be reduced at the same time.
Lighting accounts for a large part of the energy bill, ranging from 30-70% of the total energy cost. Lighting energy use represents only 5-25% of the total energy in industrial facilities
The minimum lighting level standards of the Illuminating Engineering Society (IES) should be followed to insure worker productivity and safety.
Inadequate lighting levels can decrease productivity, and they can also lead to a perception of poor indoor air quality.

## Slide 3: Components
A lighting system consists of:
light sources (lamps),
luminaires (or ﬁxtures),
and ballasts.
Each component will affect the performance, energy use and annual operating cost of the lighting system.

## Slide 4: Lamp Characteristics
Luminous Efﬁcacy: is an estimate of the light output (lumens) divided by the electrical power input (watts) under test conditions.

## Slide 5: Lamp Characteristics
Color Rendering Index: (CRI) is a relative indication of how well colors can be distinguished under the light produced by a lamp with a particular color temperature. The index runs from 0 to 1; where a high CRI indicates good color rendering.
The energy manager should not recommend changing lamp color unless nearly everyone is in favor of the proposed change.

## Slide 6: Lamp Types
Incandescent Lamps:
Render colors well, are inexpensive to purchase, easily dimmed, small, and controllable which is useful for product display.
However, they have relatively short lifespans, low efﬁcacy and are susceptible to failure from heat and vibration.
Most incandescent lamps tend to darken with age as tungsten is lost from the ﬁlament and deposited on the lamp walls.

## Slide 7: Lamp Types
Incandescent Types:
A Lamps, These lamps are low cost and commonly used in sizes of 20-1500 Watts.
Reﬂector (R) Lamps. These lamps are usually more expensive than A-lamps and offer better control of the direction in which light is cast due to a reﬂective paint on the lamp wall.
Ellipsoidal Reﬂector (ER) Lamps. These lamps cost about the same as R-lamps, but they are longer and have a focal point in front of the lamp.
Quartz-Halogen Lamps. These lamps have a short life and low efﬁcacy. They can be a good choice for areas which need lighting on an irregular basis. These lamps should not be cleaned.
Halogen Lamps. These lamps have a higher efﬁcacy and cost more than the lamps listed above and are available in many of the same lamp configurations

## Slide 10: Lamp Types
Fluorescent Lamps
Fluorescent lamps have high efﬁcacy, long life, and low surface luminance; they are cool and are available in a variety of colors.
Fluorescent lamps are available in standard, high output (HO), and very high output (VHO) conﬁgurations. The HO and VHO lamps are useful for low-temperature environments and areas where a lot of light is needed with minimal lamp space.
Energy-saving Lamps. reduce power demand and energy use by about 15%. They will also decrease light levels about 3-10%. These lamps can only be used with ballasts designed and rated for energy-saving lamps and should not be used in areas in which the temperature falls below 15°C.

## Slide 11: Lamp Types
T-Measures for Lamps. The T-measure for a ﬂuorescent lamp is the measure of the diameter of the lamp (originally in eighths of an inch).
T10 Lamps. T10 lamps typically contain phosphors which produce high efﬁcacy and color rendition. They will operate on most ballasts designed for T12 lamps.
T8 Lamps with Electronic Ballasts. T8 lamps (26 mm) produce an efﬁcacy of up to 100 lumens/Watt, the highest efﬁcacy of any ﬂuorescent lamp.
Compact Fluorescent Lamps (CFLs). It can be used to reduce energy use and power demand by over 70%. have a lifetime of at least 10,000 hours.

## Slide 15: Lamp Types
High Intensity Discharge (HID) Lamps
These lamps are relatively expensive initially but offer low life-cycle costs due to long life and high efﬁcacy.
Mercury Vapor Lamps. It offer good color rendering and low-to-moderate efﬁcacy.
Metal Halide lamps.
High Pressure Sodium (HPS) Lamps.

## Slide 17: Lamp Types
Low-Pressure Sodium (LPS) Lamps
LPS lamps offer the highest efﬁcacy of any light source (i.e., up to 180 lumens/Watt). They have a long life but are fairly large compared to HID lamps. Their size requires a larger, more complex reﬂector design to efﬁciently utilize the light produced.
LPS lamps are common in European street lighting systems.

## Slide 21: Ballasts

## Slide 22: Ballasts
A ballast is required to start and operate all discharge lamps.
Each lamp/ballast combination should have test results which state the ballast factor (BF). The lumen rating for a lamp is based on a particular lamp/ballast combination with a ballast factor of 1.0. The ballast factor indicates the light output of a particular system relative to a standard test ballast on which the lamp lumen ratings are based. For example, if a four-foot F32T8 has a rated lamp light output of 3000 lumens, and it is used with a ballast which has a ballast factor of 1.1 for the lamp/ballast combination, the system produces about 3300 lumens.

## Slide 23: Ballasts
Some electronic ballasts can be dimmed, but they also can produce signiﬁcant levels of harmonic distortion. When recommending electronic ballasts, specify ballasts with a total harmonic distortion (THD) less than 15%.

## Slide 24: MAINTAINING THE LIGHTING SYSTEM
Maintenance includes both cleaning and relamping.
Dust accumulation on lighting fixtures and on surfaces adjacent to lighting fixtures reduces light utilization by up to 40 percent and increases heat production.
Outdoor lighting has some special maintenance problems. Poorly sealed gaskets allow insects to clog the lenses of outdoor lighting fixtures.
Dead insects can completely block out light.
Overgrown vegetation can also reduce lighting levels from outside fixtures.

## Slide 26: Establishing the Lighting System Maintenance Schedule

## Slide 27: Establishing the Lighting System Maintenance Schedule
Relamping strategy
The usual strategy for replacing lamps in many facilities is to wait until a lamp burns out and then replace it (called spot relamping).
It does not consider such factors as labor costs or lumen depreciation.
It is often more economical to replace all of the fluorescent and HID lamps in a facility at one time (called group relamping).
Note that the life of a lamp is measured in hours of use rather than installed hours.
Lamp mortality at 85-100% of rated life is about twenty-five times that of lamps aged 0-70% of rated life. Therefore, fixtures should be group relamped when lamps are between 70-80% of the rated lamp life.

## Slide 28: Establishing the Lighting System Maintenance Schedule

## Slide 29: Establishing the Lighting System Maintenance Schedule

## Slide 30: Establishing the Lighting System Maintenance Schedule

## Slide 31: Establishing the Lighting System Maintenance Schedule

## Slide 32: Establishing the Lighting System Maintenance Schedule

## Slide 33: Establishing the Lighting System Maintenance Schedule

## Slide 34: Establishing the Lighting System Maintenance Schedule
Important notes:
Lamp life ratings indicate the point at which half of the lamps are likely to have failed.
Fluorescent lamp lifetimes are rated at three hours per start; HID lamps are rated at five hours per start. Operating the lamps for shorter periods will reduce lamp life.

## Slide 35: Establishing the Lighting System Maintenance Schedule
Group relamping can:
Reduce labor costs: Spot relamping can require up to 30 minutes to move furnishings or equipment, set up, replace the lamp, and put equipment away (e.g., ladder, lamps, tools). In group relamping, a fixture can usually be relamped and cleaned in 5 minutes.
Reduce lamp costs (discounts).
Allow lamp maintenance to be scheduled.
Maintain higher and more uniform lighting levels.
Reduce inventory needs.
Insure the correct lamp use: provides an opportunity to install the newest energy-efficient lamp.
Extend ballast life.
Reduce interruptions in work area.

## Slide 36: Establishing the Lighting System Maintenance Schedule

## Slide 37: Establishing the Lighting System Maintenance Schedule

## Slide 39: The Lighting Survey
The energy auditor must gather the following data: lighting needs/objectives, hours/days that lighting is required, lighting levels, type of lamps, age of lamps, age of the lighting installation, ambient environment of lighting fixtures (e.g., dust exposure, air temperature, etc.), room surface characteristics, type of ballasts, condition of fixtures, and relamping practices.

## Slide 40: The Lighting Survey
Two basic surveys should be conducted to look for savings opportunities:
To see how the facility operates while in production.
To determine the lighting practices when the facility is dormant or shut down for the night.

## Slide 41: The Lighting Survey

## Slide 42: The Lighting Survey

## Slide 43: Identifying Potential EMOS
In examining the lighting system, the energy auditor should ask three questions:
whether the light is needed;
whether the correct amount of light is being used;
what is the most cost-effective lighting technology to use to supply the correct amount and quality of light.

## Slide 44: Identifying Potential EMOS

## Slide 45: Saving Methods
Delampling:
Major savings can be obtained by removing some of the lamps that are producing excessive levels of illumination.
There is usually one ballast for each two fluorescent lamps. The ballast for rapid-start lamps will continue to consume some power even when the lamps are removed. Leaving burned-out lamps in IS (instant start) fixtures reduces ballast life.

## Slide 46: Saving Methods

## Slide 47: Saving Methods
Task lighting:
Ambient lighting levels can be reduced when adequate task lighting is supplied for the work.
Ambient lighting levels of 250 Lux or less are frequently sufficient if the individual work areas have sufficient light from task-dedicated lighting fixtures.

## Slide 48: Saving Methods

## Slide 51: Saving Methods
Relampling:
Replacing existing lamps, ballasts and luminaires with newer, because more energy-efficient models offers the potential for significant savings

## Slide 54: Saving Methods
Ballasts:
an important part of a lighting system, and each ballast uses from five to twenty percent of the power of the lamp it is associated with.
When a lamp is removed from a fixture, the ballast should usually be removed too.
Lighting control technologies:
Switches, timers, occupancy sensors, and dimmers.

## Slide 56: Saving Methods
Other lighting EMOs:
exterior lighting (use photocell), daylighting, and environmental factors.
Selecting correct lights for a new facility.